## BoQ for Quotation
Government of Nepal
Ministry of Energy, Water Resources & Irrigation
Department of Water Resources & Irrigation
Sunkoshi Marin Diversion Multipurpose Project, Sindhuli
Bill of Quantities
|  |  |  | FY: 2083/84 |  |  |  | Date: |  | 2026-07-28
[8 empty] | NRB Dollar Exchange Rate |  | 153.76
Design, Manufacture, Supply, Transportation, Erection, Testing and Commissioning of Electro Mechanical Works
SN | Particulars | Quantity | Unit | Unit Estimate Rate (USD) |  | Unit Estimate Rate (NRs) |  | Total Estimated Rate (NRs) |  | Total Estimate Amount (NRs)
|  |  |  | CIP to Custom Entry Point | Local Trans., Erec., Testing & Commissioning | CIP to Custom Entry Point | Local Trans., Erec., Testing & Commissioning | CIP to Custom Entry Point | Local Trans., Erec., Testing & Commissioning
1 | 2 | 3 | 4 | 5 | 6 | 7=5*Exc Rate | 8=6*Exc Rate | 9=3*7 | 10=3*8 | 11=9+10
A. | Mechanical Equipment
1 | Francis Turbine, Vertical Shaft with capacity 10,620 kW, 375 rpm, efficiency not less than 93 % at rated capacity, complete with all accessories, control equipment and maintenance tools | 4 | Set
1.1 | Spare Parts required for 5 years | 1 | Lot
1.2 | Turbine model test all complete | 1 | Lot
2 | Electro-Hydraulic Governors with digital controls, PID type including oil pressure system complete with all accessories, control equipment and maintenance tools | 4 | Set
2.1 | Spare Parts required for 5 years | 1 | Lot
3.1 | Main Inlet Butterfly Valves, 2.1 m diameter, double seal type, net head 52.123 m, including by-pass valve, all connecting pipe etc. complete with all accessories, control equipment and maintenance tools | 4 | Set
3.2 | Main Shutoff butterfly valve, 5.0 m diameter, double seal type including by-pass valve, all connecting pipe etc. complete with all accessories, control equipment and maintenance tools | 1 | Set
3.3 | Spare Parts required for 5 years | 1 | Lot
4 | Cooling Water System including valves, pumps, strainers, piping, control equipment etc. for units complete with all accessories, control equipment and maintenance tools | 1 | Lot
4.1 | Spare Parts required for 5 years | 1 | Lot
5 | Clean Water System including valves, pumps, strainers, piping, tanks etc. complete with all accessories, control equipment and maintenance tools | 1 | Lot
5.1 | Spare Parts required for 5 years | 1 | Lot
6 | Dewatering and Drainage System including pumps, piping, valves etc. complete with all accessories, control equipment and maintenance tools | 1 | Lot
6.1 | Spare Parts required for 5 years | 1 | Lot
7.1 | Powerhouse, Overhead Electric Travelling Cranes including main hoist of 50 ton and auxiliary hoist of 10 ton, complete with all accessories, control equipment and maintenance tools | 1 | Lot
7.2 | Main Shutoff Valve, Overhead Electric Travelling Cranes including main hoist of 100 ton and auxiliary hoist of 10 ton, complete with all accessories, control equipment and maintenance tools | 1 | Lot
7.3 | Spare Parts required for 5 years | 1 | Lot
8 | Oil Handling and Treatment System including oil pump, tanks and oil purification equipment (For hydraulic oil and transformer oil) etc. complete with all accessories, control equipment and maintenance tools | 1 | Lot
8.1 | Spare Parts required for 5 years | 1 | Lot
9 | Compressed Air System, including low pressure compressors, receivers, dryers with all accessories, control equipment and maintenance tools | 1 | Lot
9.1 | Spare Parts required for 5 years | 1 | Lot
10 | Firefighting System including pumps, piping, valves etc. complete with all accessories, control equipment and maintenace tools | 1 | Lot
10.1 | Spare Parts required for 5 years | 1 | Lot
11 | HVAC System including Air Conditioning units, piping, valves, ducting etc. complete with all accessories, control equipment and maintenance tools | 1 | Lot
11.1 | Spare Parts required for 5 years | 1 | Lot
12 | Measurement System for Hydraulic Quantities complete with all accessories, control equipment and maintenance tools | 1 | Lot
12.1 | Spare Parts required for 5 years | 1 | Lot
13 | Mechanical Workshop Facilites complete with all machinery, tools, devices etc. | 1 | Lot
13.1 | Spare Parts required for 5 years | 1 | Lot
14 | Powerhouse Elevator complete with all accessories, control equipment and maintenance tools | 1 | Lot
B. | Electrical Equipment
1 | Alternating Current Generator
1.1 | Synchronous Alternating Current Generators, Vertical Shaft, 12250 kVA, 11 kV, 375 rpm, efficiency not less than 98 % at rated capacity complete with all accessories instruments, control equipment, Spares and maintenance tools | 4 | Set
1.2 | Spare Parts required for 5 years | 1 | lot
2 | Excitation System
2.1 | Static Excitation system complete with excitation transformer with its cubicle, AVR and Spares | 4 | Set
2.2 | Spare Parts required for 5 years | 1 | lot
3 | Medium Voltage Switch Gear complete as per the specification not limited to as mentioned hereunder:
3.1 | 11 kV generator circuit breaker assemblies all complete including accessories | 4 | set
3.2 | 11 kV feeder assemblies for connecting main transformers all complete including accessories | 4 | set
3.3 | 11 kV feeder assembly for supply from NEA transformer all complete including accessories | 1 | set
3.4 | 11 kV feeder assemblies for station service all complete including accessories | 2 | set
3.5 | 11 kV bus sectionalizer feeder assembly all complete including accessories | 1 | set
3.6 | Spare Parts required for 5 years | 1 | lot
4 | Neutral Grounding Equipments
4.1 | Neutral grounding system with necessary grounding transformer, resistor, and cubicle, Spares | 4 | set
4.2 | Spare Parts required for 5 years | 1 | lot
5 | Main Transformers
5.1 | Step Up Transformer 11/132/√3 kV, 29000/37000 kVA, ONAN/ONAF type, efficiency not less than 99%, complete with all accessories, control equipment and Spares | 2 | set
5.2 | Spare Parts required for 5 years | 1 | lot
6 | Station Transformers and Other Transformers complete with all accessories, control equipment and maintenance tools:
6.1 | 11/0.4 kV, 450 kVA, indoor type station service transformer | 2 | Set
6.2 | 11/33 kV, 1000 kVA ONAN outdoor type NEA supply distribution transformer | 1 | Set
6.3 | Spare Parts required for 5 years | 1 | lot
7 | 132 KV AIS Switchgear complete with all accessories as mentioned
7.1 | 145 kV ,1250 A , 40 kA SF6 Circuit Breaker with all accessories | 4 | set
7.2 | 145 kV ,1250 A Disconnecting Switches with earthing -complete with all accessories as specified | 4 | set
7.3 | 145 kV ,1250 A Disconnecting Switches without earthing -complete with all accessories | 4 | set
7.4 | 120 kV lightning Arrester complete with all accessories | 12 | set
7.5 | Switchyard steel structures for individual equipments, busbars, outgoing circuits, shielding wire supports, insulators, conductors complete with all accessories | 1 | lot
7.6 | Switchgear miscellaneous materials such as busbars, insulator and fittings, shielding wires etc all complete | 1 | lot
7.7 | 132 kV Potential (Voltage) Transformer complete with all accessories | 6 | set
7.8 | 132 kV Potential (Voltage) Transformer complete with all accessories | 6 | set
7.9 | 132 kV Bus Coupler complete with all accessories | 1 | set
7.1 | 132 kV Current Transformer complete with all accessories | 12 | set
7.11 | Spare Parts required for 5 years | 1 | lot
8 | AC Auxilliary Supply System
8.1 | AC auxiliary supply system consisting of, but not limited to, Main Switchboard, Unit Auxiliary Distribution Boards, Common Load Distribution Boards, Sub Distribution Boards in Power house and Headworks all complete | 1 | lot
8.2 | Spare Parts required for 5 years | 1 | lot
9 | Diesel Generator
9.1 | Diesel Generator System of rated capacity 200kVA, 0.4kV and 1500rpm all complete , including accessories | 2 | set
9.3 | Spare Parts required for 5 years | 1 | lot
10 | DC Supply System
10.1 | DC Supply System consisting of Battery, Battery Chargers, Distribution Boards, Inverters/UPS etc all complete for Powerhouse and Headworks | 1 | lot
10.2 | Spare Parts required for 5 years | 1 | lot
11 | MV LV Cables
11.1 | 12 kV , XLPE , single phase, Power cables and necessary equipments all complete | 1 | lot
11.2 | 600V Power Cables and necessary equipment all complete | 1 | lot
11.3 | Control, instrumentation and communication cables with accessories all complete | 1 | lot
11.4 | Necessary cable trays, conduits, fittings, termination kits and accessories | 1 | lot
11.5 | Spare Parts required for 5 years | 1 | lot
12 | Protection System
12.1 | Complete Main and Backup protection for the power plant but not limited to the protection of (i) Generators and Cables (ii) Power Transformers (iii) Transmission Line (iv) Auxiliary Supply Systems (v) Distribution System (vi) Powerhouse end Outdoor 132kV AIS (vii) AIS system at the Interconnection system | 1 | lot
12.2 | Spare Parts required for 5 years | 1 | lot
13 | Control & Automation
13.1 | Power Plant Automation and Control System complete with all accessories, control equipment and maintenance tools | 1 | lot
13.2 | Spare Parts required for 5 years | 1 | lot
14 | Communication System
14.1 | Communication System including but not limited to telephone and intercommunication system, optical communication system, radio communication system complete with all accessories, equipments and maintenance tools | 1 | lot
14.2 | Spare Parts required for 5 years | 1 | lot
15 | Security System
15.1 | Security System including but not limited to Closed Circuit Television, Access Control System, recorders, fibre optic cables, power supply units complete with all accessories, equipments and maintenance tools | 1 | lot
15.2 | Spare Parts required for 5 years | 1 | lot
16 | Earthing System
16.1 | Earthing System including but not limited to supply and design of earthing materials for Sub-grade earthing system, above ground indoor and outdoor earthing system, potential gradient control, lightning protections complete with all accessories, equipments and maintenance tools | 1 | lot
16.2 | Spare Parts required for 5 years | 1 | lot
17 | Lighting System
17.1 | Lighting System including but not limited to supply and design of small power installations in powerhouse and pertinent buildings and structures, headwors and other structures of the power plant complete with all accessories, equipments and maintenance tools | 1 | lot
17.2 | Spare Parts required for 5 years | 1 | lot
18 | Electrical Workshop
18.1 | Electrical Workshop Facilites complete with all machinery, tools, devices and accessories. | 1 | lot
18.2 | Spare Parts required for 5 years | 1 | lot
19 | Nawalpur Line Bay complete with all accessories as mentioned
19.1 | 145 kV ,1250 A ,31.5 kA SF6 Circuit Breaker with all accessories | 2 | set
19.2 | 145 kV ,1250 A Disconnecting Switches with earthing -complete with all accessories | 2 | set
19.3 | 145 kV ,1250 A Disconnecting Switches without earthing complete with all accessories | 2 | set
19.5 | 120 kV lightning Arrester complete with all accessories for single bay | 6 | set
19.6 | Line Control and protection equipment with necessary numerical relays and panels with complete indication and alarm systems all complete | 1 | lot
19.7 | Switchyard steel structures for individual equipments, busbars, outgoing circuits, shielding wire supports, insulators, conductors complete with all accessories | 1 | lot
19.8 | Switchgear miscellaneous materials such as busbars, insulator and fittings, shielding wires etc all complete. | 1 | lot
10.9 | Complete grounding of SMDMP line bay | 1 | lot
19.1 | 132 kV Potential (Voltage) Transformer complete with all accessories | 6 | set
19.11 | 132 kV Current Transformer complete with all accessories | 6 | set
19.12 | Main and Check Tariff Meter of Class 0.1 with TVM panel conforming to the latest Grid Code | 2 | set
19.13 | 132 kV Potential Transformer complete with all accessories as Bus PT | 3 | set
19.14 | Spare Parts required for 5 years | 1 | lot
Total Excluding VAT